## Instructions
Sodium Zeolite Water Softener Calculation Instructions
1) Enter the required data on the each worksheet.
- All required data is shown in red text and may be changed.
- All assumptions are shown in green text and may be changed. (Assumptions are based upon accepted rules of thumb.)
- All equations are shown in blue text and cannot be changed.
2) Cells with a red triangle in the upper right corner has more information available. Position the mouse pointer over the square and a comment box will appear.
3) All worksheets are protected. This means that only red and green text cells are unlocked and can be changed. TAB and ENTER can be used to navigate through the unlocked cells. (If you really must make a change to a locked cell, select TOOLS from the menu bar, select PROTECTION from the drop-down menu, and then select UNPROTECT SHEET.)
4) This file is a read-only file. This is to protect the integrity of the original file. When you enter your data and try to save the file, you will need to rename the file.

## Capacity
Sodium Zeolite Water Softener
Capacity Calculation
Total Hardness | 300 | ppm as CaCO3
Iron | 0 | ppm as Fe
Cubic Feet of Resin | 40 | ft3
Exchange Capacity | 27000 | gr/ft3
Expected % Capacity | 90% | %
Softening Capacity | 55404 | gallons
Note on A5: Factoring in Iron Iron can be exchanged on SAC softener resin too. It is typically assumed that 1 ppm Fe equals 2 ppm Total hardness.
Note on A7: Typical Strong Acid Cation Resin Softening Exchange Capacities Salt (lb/ft3) Capacity (gr/ft3) 6 21,000 8 24,000 10 27,000 12 29,000 15 30,000 For more exact exchange capacities, the resin specifications should be obtained from the manufacturer. Reference: Purolite Water Softening Resin Guide, Chubb Michaud, Purolite, 2007
Note on A8: Expected % Capacity To minimize hardness leakage and complete resin bed exhaustion, water softeners are usually run up to a certain percentage of theoretical full capacity. A typical number used is 90%.

## Brine Recovery
Brine Recovery
Salt Savings Calculation
Salt Dosage | 10 | lb/ft3
Volume of Water Softened | 5250000 | gal/yr
Total Hardness | 300 | ppm as CaCO3
Iron | 0 | ppm as Fe
Cubic Feet of Resin | 40 | ft3
Cost of Salt | 0.9 | cost/lb
Exchange Capacity | 27000 | gr/ft3
Expected % Capacity | 90% | %
Assumed Salt Usage Reduction | 20% | %
Softening Capacity | 55404 | gallons
Regenerations per year | 94.7585 | regenerations/yr
Annual Salt Usage | 37903.4005 | lbs/yr
New Salt Usage | 30322.7204 | lbs/yr
Salt Savings | 7580.6801 | lbs/yr
Money Saved on Salt | 6822.6121 | $
Note on A17: Factoring in Iron Iron can be exchanged on SAC softener resin too. It is typically assumed that 1 ppm Fe equals 2 ppm Total hardness.
Note on A20: Typical Strong Acid Cation Resin Softening Exchange Capacities Salt (lb/ft3) Capacity (gr/ft3) 6 21,000 8 24,000 10 27,000 12 29,000 15 30,000 For more exact exchange capacities, the resin specifications should be obtained from the manufacturer. Reference: Purolite Water Softening Resin Guide, Chubb Michaud, Purolite, 2007
Note on A21: Expected % Capacity To minimize hardness leakage and complete resin bed exhaustion, water softeners are usually run up to a certain percentage of theoretical full capacity. A typical number used is 90%.
Note on A22: Salt Usage: The literature indicates that most brine recovery systems save approximately 20-25% on salt depending on the settings and type of system.
Brine recovery is known by many names including brine reuse, brine recycle, and brine reclamation, but all perform the same task. These systems return a portion of used dilute brine, also known as "sweet brine" , to the brine tank in a water softening system, and the amount of brine directed to the brine tank is directly proportional to the amount of salt that can be saved using this process. Brine reclamation can be time-based or conductivity based, and depending on the system can result in a 20 - 25% savings on salt alone.
*Note: The reviews have been mixed on how efficient the process is, and this document is only meant to be an informational tool, not an endorsement of the process.

## Survey Form
Softener Survey Form
| Parameter | Manufacturer Specifications | Resin Specifications | Actual Data
1 | Resin Designation (Name)
2 | Quantity of resin in unit (ft3)
3 | Unit Diameter (ft)
4 | Unit surface area (ft2)
5 | Resin bed depth (ft)
6 | Unit freeboard (ft)
7 | Throughput (gallons)
8 | Pressure drop across unit (psi)
9 | Service flow rate (gpm)
10 | Service flow rate (gpm/ft2)
11 | Backwash water temp (F)
12 | Backwash flow rate (gpm)
13 | Backwash flow rate (gpm/ft2)
14 | Backwash time (min)
15 | Quantity of salt used (lbs)
16 | Quantity of salt used (lb/ft3)
17 | Expected leakage (mg/L)
18 | Concentrated brine solution strength (%)
19 | Dilute brine solution strength (%)
20 | Dilute brine flow rate (gpm)
21 | Dilute brine flow rate (gpm/ft3)
22 | Dilute brine flow time (min)
23 | Dilute brine contact time (min)
24 | Slow rinse flow rate (gpm)
25 | Slow rinse flow rate (gpm/ft3)
26 | Slow rinse time (min)
27 | Slow rinse volume (gal/ft3)
28 | Fast rinse flow (gpm)
29 | Fast rinse flow (gpm/ft3)
30 | Fast rinse time (min)
31 | Fast rinse volume (gal/ft3)
32 | Total rinse volume (gal)
33 | Total rinse required (gal/ft3)

## Elution Study
Elution Study
Time | Salometer Degrees (%)
3 | 0
6 | 2 |  | 0 | 30
9 | 6 |  | 81 | 30
12 | 12
15 | 19
18 | 25
21 | 30
24 | 33
27 | 35
30 | 35
33 | 35
36 | 35
39 | 35
42 | 35
45 | 35
48 | 35
51 | 33
54 | 28
57 | 18
60 | 11
63 | 5
66 | 3 | Notes:
69 | 0 | "Enough, for long enough." -- Allan Bassett, 2001
72 | 0 | 30 salometer degress for 30 minutes
75 | 0 | Sample every 2 to 3 minutes
78 | 0
81 | 0

## Interpretive Curves
Elution Study Interpretive Curves
| Time | Salom.
| 0 | 0
| 5 | 0
| 10 | 2
| 15 | 11
| 20 | 29
| 25 | 32
| 30 | 32
| 35 | 32
| 40 | 32
| 45 | 32
| 50 | 30
| 55 | 20
| 60 | 0
| Time | Salom.
| 0 | 0
| 5 | 0
| 10 | 0
| 15 | 0
| 20 | 10
| 25 | 20
| 30 | 30
| 35 | 40
| 40 | 48
| 45 | 54
| 50 | 59
| 55 | 63
| 60 | 61
| 65 | 5
| 70 | 0
| Time | Salom.
| 0 | 0
| 5 | 8
| 10 | 15
| 15 | 22
| 20 | 29
| 25 | 35
| 30 | 40
| 35 | 43
| 40 | 45
| 45 | 45
| 50 | 44
| 55 | 42
| 60 | 35
| 65 | 20
| 70 | 0
| Time | Salom.
| 0 | 0
| 5 | 1
| 10 | 4
| 15 | 33
| 20 | 46
| 25 | 48
| 30 | 40
| 35 | 22
| 40 | 7
| 45 | 0
| 50 | 0
| 55 | 0
| 60 | 0
| 65 | 0
| 70 | 0
| Time | Salom.
| 0 | 0
| 5 | 12
| 10 | 33
| 15 | 36
| 20 | 32
| 25 | 2
| 30 | 0
| 35 | 0
| 40 | 0
| 45 | 0
| 50 | 0
| 55 | 0
| 60 | 0
| 65 | 0
| 70 | 0
| Time | Salom.
| 0 | 0
| 5 | 1
| 10 | 3
| 15 | 16
| 20 | 18
| 25 | 18
| 30 | 18
| 35 | 18
| 40 | 18
| 45 | 18
| 50 | 18
| 55 | 17
| 60 | 10
| 65 | 1
| 70 | 0
| Time | Salom.
| 0 | 0
| 5 | 1
| 10 | 2
| 15 | 3
| 20 | 4
| 25 | 6
| 30 | 13
| 35 | 17
| 40 | 19
| 45 | 18
| 50 | 13
| 55 | 2
| 60 | 0
| 65 | 0
| 70 | 0
| Time | Salom.
| 0 | 0
| 5 | 1
| 10 | 3
| 15 | 11
| 20 | 29
| 25 | 31
| 30 | 31
| 35 | 31
| 40 | 30
| 45 | 25
| 47 | 0
55
60
65
70
| Time | A Salom. | B Salom.
| 0 | 0 | 0
| 5 | 10 | 10
| 10 | 30 | 28
| 15 | 63 | 45
| 20 | 71 | 51
| 25 | 73 | 53
| 30 | 71 | 51
| 35 | 63 | 45
| 40 | 30 | 28
| 45 | 10 | 10
| 50 | 0 | 0
The blue line represents regeneration with saturated brine. The red line represents regeneration with dilute brine.
Brining cycle interrupted by a premature rinse cycle.
Insufficient brine strength and contact time. Possible remedies are to increase brine draw time, decrease dilution water, and decrease slow rinse rate.
Brine eductor draws too slowly. It should be adjusted to draw brine faster.
Insufficient brine. Increase brine draw time.
Brine eductor draws too quickly. It should be adjusted to draw brine more slowly.
Using more salt than necessary. Reduce brine draw to save salt.
Using more salt than necessary. Reduce the brine draw and perhaps decrease slow rinse rate.
A good regeneration that uses a minimum of salt.

## Troubleshooting
Troubleshooting
Problem | Possible Causes | Check | Action to Correct
Short Runs
Continual short runs. | Change in raw water hardness. | Influent hardness. (You should have a good history of this parameter.) | Consider softer water source or higher regeneration level.
| Poor regenerations. | Check regeneration timer setup and flowrates. | Readjust flows and/or brine strengths based on review and elution study. Be sure backwash flow rate is adequate to expand the bed. Don't forget to inspect and monitor brine system during elution study.
Elution study.
| Channeling due to bed fouling or distributor problem. | Influent turbidity history. | Improve performance of equipment ahead of the softener.
|  | Bed inspection reveals precipitation of solids. | Check Backwash. Replace/repair distributor or strainers.
| Resin fouling. | Resin analysis. | Reduce source of foulant. Apply appropriate cleaning procedures.
| Loss of resin. | Excessive backwash flow rate. | Adjust flow rate.
|  | Collector strainer problems. | Fix strainers.
|  | Check for resin in subfill. | Repair distributor element. Replace subfill contaminated with resin.
|  | Chlorine degradation of resin. | Consider dechlorinating the source water.
High Hardness in Product Water
| Raw water bypassing unit. | Test water before and after valve. | Repair or replace valve.
| Resin fouling. | Measure Ca/Mg ratio before and after unit. (Note: the hardness levels in the product water may be too low for this test to be viable.) | Different ratio before and after may indicate resin foulant. Check pretreatment.
| Deteriorating regeneration practices. | Elution study. | Revise procedure. (Don't forget to inspect and monitor brine system while conducting elution study.)
| Increased hardness in source water. | Influent hardness. (You should have a good history of this parameter.) | Consider softer water source or higher regeneration level.
| Previous complete hardness breakthrough. | Check history. | Perform a double regeneration.
High Pressure Drop
| Bed Fouling. | Look for channeling or solids on bed surface. | Adjust current backwash flow rate for current water temperature.
| Poor backwash. | Backwash flow rate. | Adjust current backwash flow rate for current water temperature.
| Plugged under drain strainers. | Inspect strainers. | Repair and/or clean. Could affect softener flowrate too.
| Deteriorating resin. | Look at moisture content of beads, look for resin fines. | Possible resin replacement.
| Valve blockage. | Review history of pressure drop. | Check and replace/repair valve.
| Gauge(s) wrong. | Interchange gauges with another unit. | Replace if necessary.

## Backwash
Backwash vs. Temperature
A proper backwash is necessary to ensure efficient softener operation. Backwashing loosens the bed, cleans and classifies the resin, minimizes pressure drop, and maintains an even water flow across the cross sectional area of the resin bed. Backwash flow rates must be sufficient to expand the resin bed by 50% and typically last around 10 minutes or more. It is very important to take into account season backwash water temperature variations to ensure an effective backwash.
The temperature-corrected backwash flowrates in the table below are typical, but manufacturer resin specifications should always be consulted for actual design numbers.
Vessel Diameter (feet) | Cross Sectional Area (sq ft) | Backwash Flowrates (gpm)
|  | 40° F | 50° F | 60° F | 70° F | 80° F | 90° F
2 | 3.14 | 14 | 16 | 18 | 20 | 22 | 23
2.5 | 4.9062 | 22 | 24 | 28 | 30 | 34 | 36
3 | 7.065 | 32 | 36 | 40 | 44 | 48 | 52
3.5 | 9.6163 | 44 | 48 | 56 | 60 | 66 | 72
4 | 12.56 | 58 | 64 | 72 | 78 | 86 | 94
4.5 | 15.8963 | 72 | 80 | 92 | 100 | 108 | 118
5 | 19.625 | 88 | 98 | 112 | 122 | 134 | 146
5.5 | 23.7462 | 108 | 120 | 136 | 148 | 162 | 176
6 | 28.26 | 128 | 142 | 162 | 176 | 192 | 210
6.5 | 33.1662 | 150 | 166 | 190 | 206 | 226 | 246
7 | 38.465 | 174 | 194 | 220 | 240 | 262 | 286
7.5 | 44.1562 | 200 | 222 | 252 | 274 | 300 | 328
8 | 50.24 | 226 | 252 | 288 | 312 | 342 | 372
8.5 | 56.7163 | 256 | 284 | 324 | 352 | 386 | 420
9 | 63.585 | 288 | 318 | 364 | 396 | 434 | 470
9.5 | 70.8462 | 320 | 356 | 404 | 440 | 482 | 524
10 | 78.5 | 354 | 394 | 448 | 488 | 534 | 582
10.5 | 86.5463 | 390 | 434 | 494 | 538 | 590 | 640
11 | 94.985 | 428 | 476 | 542 | 590 | 646 | 704

## NaCl Properties
Sodium Chloride Brine Characteristics Table
The brine table below applies to brine tested at 60°F and using a 60°F Salometer. For reading brine tested at other temperatures, the observed Salometer (60°F) must be converted before using in the table. For practical purposes, add one degree salometer for each ten degrees above 60°F and deduct one degree salometer for each ten degrees below 60°F.
Salometer Degrees | Specific Gravity | Baumè Degrees | % Sodium Chloride by Weight | Lbs. NaCl per gal. Brine | Lbs Water per gal. Brine | Gal. Water per gal. brine | Lbs. Salt per gal. water | Freeze Point °F
0 | 1 | 0 | 0 | 0 | 8.328 | 1 | 0 | 32
2 | 1.004 | 0.6 | 0.528 | 0.044 | 8.318 | 0.999 | 0.044 | 31.5
4 | 1.007 | 1.1 | 1.056 | 0.089 | 8.297 | 0.996 | 0.089 | 31.1
6 | 1.011 | 1.6 | 1.584 | 0.133 | 8.287 | 0.995 | 0.134 | 30.5
8 | 1.015 | 2.1 | 2.112 | 0.178 | 8.275 | 0.993 | 0.179 | 30
10 | 1.091 | 2.7 | 2.64 | 0.224 | 8.262 | 0.992 | 0.226 | 29.3
12 | 1.023 | 3.3 | 3.167 | 0.27 | 8.25 | 0.99 | 0.273 | 28.8
14 | 1.026 | 3.7 | 3.695 | 0.316 | 8.229 | 0.988 | 0.32 | 28.2
16 | 1.03 | 4.2 | 4.223 | 0.362 | 8.216 | 0.987 | 0.367 | 27.6
18 | 1.034 | 4.8 | 4.751 | 0.409 | 8.202 | 0.985 | 0.415 | 27
20 | 1.038 | 5.3 | 5.279 | 0.456 | 8.188 | 0.983 | 0.464 | 26.2
22 | 1.042 | 5.8 | 5.807 | 0.503 | 8.175 | 0.982 | 0.512 | 25.7
24 | 1.046 | 6.4 | 6.335 | 0.552 | 8.159 | 0.98 | 0.563 | 25.3
26 | 1.05 | 6.9 | 6.863 | 0.6 | 8.144 | 0.978 | 0.614 | 24.4
28 | 1.054 | 7.4 | 7.391 | 0.649 | 8.129 | 0.976 | 0.665 | 23.7
30 | 1.058 | 7.9 | 7.919 | 0.698 | 8.113 | 0.974 | 0.716 | 23
32 | 1.062 | 8.5 | 8.446 | 0.747 | 8.097 | 0.972 | 0.768 | 22.3
34 | 1.066 | 9 | 8.974 | 0.797 | 8.081 | 0.97 | 0.821 | 21.6
36 | 1.07 | 9.5 | 9.502 | 0.847 | 8.064 | 0.968 | 0.875 | 20.9
38 | 1.074 | 10 | 10.03 | 0.897 | 8.047 | 0.966 | 0.928 | 20.2
40 | 1.078 | 10.5 | 10.558 | 0.948 | 8.03 | 0.964 | 0.983 | 19.2
42 | 1.082 | 11 | 11.086 | 0.999 | 8.012 | 0.962 | 1.039 | 18.7
44 | 1.086 | 11.5 | 11.614 | 1.05 | 7.994 | 0.96 | 1.094 | 17.9
46 | 1.09 | 12 | 12.142 | 1.102 | 7.976 | 0.958 | 1.151 | 17.1
48 | 1.094 | 12.5 | 12.67 | 1.154 | 7.957 | 0.955 | 1.208 | 16.2
50 | 1.098 | 12.9 | 13.198 | 1.207 | 7.937 | 0.953 | 1.266 | 15.4
52 | 1.102 | 13.4 | 13.725 | 1.26 | 7.918 | 0.951 | 1.325 | 14.5
54 | 1.106 | 13.9 | 14.253 | 1.313 | 7.898 | 0.948 | 1.385 | 13.7
56 | 1.11 | 14.4 | 14.781 | 1.366 | 7.878 | 0.946 | 1.444 | 12.8
58 | 1.114 | 14.8 | 15.309 | 1.42 | 7.858 | 0.943 | 1.505 | 11.8
60 | 1.118 | 15.3 | 15.837 | 1.475 | 7.836 | 0.941 | 1.568 | 10.9
62 | 1.122 | 15.8 | 16.365 | 1.529 | 7.815 | 0.938 | 1.629 | 9.9
64 | 1.126 | 16.2 | 16.893 | 1.584 | 7.794 | 0.935 | 1.692 | 8.9
66 | 1.13 | 16.7 | 17.421 | 1.639 | 7.772 | 0.933 | 1.756 | 7.9
68 | 1.135 | 17.2 | 17.949 | 1.697 | 7.755 | 0.931 | 1.822 | 6.8
70 | 1.139 | 17.7 | 18.477 | 1.753 | 7.733 | 0.929 | 1.888 | 5.2
72 | 1.143 | 18.1 | 19.004 | 1.809 | 7.71 | 0.926 | 1.954 | 4.6
74 | 1.147 | 18.6 | 19.532 | 1.866 | 7.686 | 0.923 | 2.022 | 3.4
76 | 1.152 | 19.1 | 20.06 | 1.925 | 7.669 | 0.921 | 2.091 | 2.2
78 | 1.156 | 19.6 | 20.588 | 1.982 | 7.645 | 0.918 | 2.159 | 1
80 | 1.16 | 20 | 21.116 | 2.04 | 7.62 | 0.915 | 2.229 | –.4
82 | 1.164 | 20.4 | 21.644 | 2.098 | 7.596 | 0.912 | 2.3 | –1.6
84 | 1.169 | 21 | 22.172 | 2.158 | 7.577 | 0.91 | 2.372 | –3.0
86 | 1.173 | 21.4 | 22.7 | 2.218 | 7.551 | 0.907 | 2.446 | –4.4
88 | 1.178 | 21.9 | 23.228 | 2.279 | 7.531 | 0.904 | 2.52 | –5.8
88.3 | 1.179 | 22 | 23.31 | 2.288 | 7.528 | 0.904 | 2.531 | –6.0
90 | 1.182 | 22.3 | 23.755 | 2.338 | 7.506 | 0.901 | 2.594 | –1.1
92 | 1.186 | 22.7 | 24.283 | 2.398 | 7.479 | 0.898 | 2.67 | 4.8
94 | 1.191 | 23.3 | 24.811 | 2.459 | 7.46 | 0.896 | 2.745 | 11.1
95 | 1.193 | 23.5 | 25.075 | 2.491 | 7.444 | 0.894 | 2.787 | 14.4
96 | 1.195 | 23.7 | 25.339 | 2.522 | 7.43 | 0.892 | 2.827 | 18.3
97 | 1.197 | 23.9 | 25.603 | 2.552 | 7.417 | 0.891 | 2.865 | 21.6
98 | 1.2 | 24.2 | 25.867 | 2.595 | 7.409 | 0.89 | 2.906 | 25.5
99 | 1.202 | 24.4 | 26.131 | 2.616 | 7.394 | 0.888 | 2.947 | 29.8
100 | 1.204 | 24.6 | 26.395 | 2.647 | 7.38 | 0.886 | 2.987
Eutectic Point - is that solution of sodium chloride with the lowest freezing point (–6°F). Brines stronger than 88.3° Salometer deposit excess sodium chloride as dihydrate when cooled to freezing point temperatures listed and freeze at the eutectic point.

## Resin Analysis
Resin Analysis
Typical Strong Acid Cation Analysis Parameters
Total Capacity (meq/mL): | 1.9-2 for new resin
Water Retention (%): | 45-48% (chlorine degradation will increase this number)
Foulant - Iron as Fe (g/cu ft): | >9 is high
Percent Broken Beads: | >25% (macro) and >20% (gel) indicates need for replacement
Note on A5: Total Exchange Capacity Exchange capacities are determined for either cation or anion resins. Exchange capacity determinations require precise work, close attention, and may vary in time required from 2 to 12 hours. Tested exchange capacities are compared to new resin specifications to determine the current useful operating life of the resin. When capacities have significantly decreased, replacement or cleaning of the resin is indicated. When the exchange capacity for resins falls below 75 percent of new resin capacities, replacement should be considered when the physical condition of the resin is found to be poor. Cleaning of the resin may be considered when the physical condition of the resin appears satisfactory, but fouling has affected performance.
Note on A6: Water Retention or Moisture Content Moisture content and density data can be used to indicate the physical condition of the resin beads. As the beads degrade, the moisture content will increase and the density will decrease. The moisture content is obtained by collecting, via vacuum filtration, a sample of regenerated resin. A portion of the resin sample is then accurately weighed, dried in an oven overnight, reweighed, and the moisture content calculated. The percent moisture content for cation resin is a direct measure of the crosslinking. An increase in moisture content indicates de-crosslinking has begun. Excessive de-crosslinking results in a loss of exchange sites and channeling resulting in a poor quality effluent. When the percent moisture exceeds 115 to 125 percent of new resin values, replacement of the resin should be considered.
Sampling Advice
According to some resin manufacturers, over 90% of the resin samples sent for analysis are good, and there is no reason for sending the sample. The first steps you should take before requesting a resin analysis are:
1. What is the age of the resin? If it is relatively new, it is probably physically okay.
2. Have elution studies been run? Has the theoretical capacity been compared to actual? If they're seeing proper regeneration and getting good capacity, the resin is good.
3. Have you visually inspected the resin? Are the beads solid and round? Look under a magnifying glass. Are most beads solid with few cracks? If it is mushy and/or there seems to be a lot of fines or cracks, it probably should be analyzed.
4. What color is it? What color was new resin?
5. Typically, an analysis should be performed when we have a problem such as capacity or fouling and cannot determine the problems in the field.
Sampling Resin
1. Samples must be representative of the resin bed and should be a core sample.
2. Forms and labels must be filled out as completely as possible.
3. Samples for analysis should be taken for a good reason. Business sense should be applied.

## Regenerant Water
Regenerant Wastewater Characteristics
Influent Water Characteristics
| Calcium Hardness | 133 | ppm as CaCO3
| Magnesium Hardness | 66 | ppm as CaCO3
| Salt Dosage | 10 | lb/ft3
| Exchange Capacity | 27000 | gr/ft3
| Cubic Feet of Resin | 100 | ft3
| Regenerant Water Rate | 60 | gal/ft3
| Expected % Capacity | 90%
Regeneration Water Characteristics
| Calcium Hardness | 4628.6005 | ppm as CaCO3 | Softener Capacity | 2700000 | gr
| Magnesium Hardness | 2296.8995 | ppm as CaCO3 | Total Hardness in Regen Water | 405 | gr/gallon
| Chlorides | 12132.5052 | ppm as Cl- | Total Hardness in Regen Water | 6925.5 | ppm as CaCO3
| Sodium | 10797.469 | ppm as Na | Total Calcium in Regen Water | 4628.6005 | ppm as CaCO3 |  | 4628.6005
|  |  |  | Total Magnesium in Regen Water | 2296.8995 | ppm as CaCO3 |  | 2296.8995
Regeneration Water Volume
| Volume | 6000 | gallons | lb salt used | 1000 | lb NaCl
|  |  |  | lb Cl in regen water | 606.6253 | lb Cl |  | Na | 22.99 | g/mol | 39.34%
|  |  |  | Cl in regen water | 12132.5052 | ppm Cl | 12132.5052 | Cl | 35.453 | g/mol | 60.66%
|  |  |  | lb Na in regen water | 393.3747 | lb Na |  | NaCl | 58.443
|  |  |  | ppm Na possible in regen water | 7867.4948 | ppm Na
|  |  |  | ppm Na possible in regen water | 17151.1387 | ppm Na as CaCO3
|  |  |  | Na left on resin beads | 13851 | ppm Na as CaCO3
|  |  |  | Na left on resin beads | 6353.6697 | ppm Na
|  |  |  | Na left in regen water | 10797.469 | ppm Na | 10797.469
Note on B7: Typical Strong Acid Cation Resin Softening Exchange Capacities Salt (lb/ft3) Capacity (gr/ft3) 6 21,000 8 24,000 10 27,000 12 29,000 15 30,000 For more exact exchange capacities, the resin specifications should be obtained from the manufacturer. Reference: Purolite Water Softening Resin Guide, Chubb Michaud, Purolite, 2007
Note on B9: Typically, softeners use 60 gallons of water per cubic foot resin for regeneration.
Note on B10: Expected % Capacity To minimize hardness leakage and complete resin bed exhaustion, water softeners are usually run up to a certain percentage of theoretical full capacity. A typical number used is 90%.
Note on B13: This is the component level above the background level already present in the regeneration water.
Note on B14: This is the component level above the background level already present in the regeneration water.
Note on B15: This is the component level above the background level already present in the regeneration water.
Note on B16: This is the component level above the background level already present in the regeneration water. The calculation takes into account the sodium left on the resin beads during regeneration.

## References
References
How to Survey a Sodium Zeolite Water Softener, Allan Bassett, The Analyst, Winter 2001
Procedures of Industrial Water Treatment, Jim Tanis, Ltan, 1st Edition, 1987
AWT Technical Reference & Training Manual, Association of Water Technologies, Inc., Copyright 2001
Betz Handbook of Industrial Water Treatment, Betz Laboratories, Inc., Copyright 1991, ninth edition
Crown Solutions Ion Exchange Manual, Crown Solutions Co, LLC, Copyright 1996
Contributors
Allan Bassett, CWT, Bassett Air Quality, Inc.
Chris Golden, CWT, Taylor Technologies, Inc.
Casey Walton, CWT, Walton Technologies, LLC
Les Davis, CWT, All Phase Consulting, LLC
James McDonald, CWT, Crown EG
Taylor Pair, Crown EG